## README
Home Energy Audit [2] - Dorm Room Energy & Carbon Audit Workbook
Jayash Sahu ¦ SEE8115 ¦ Hall 13, CityU Lee Shau Kee Student Residence Village, Room 1003B, 10/F ¦ Ma On Shan, New Territories, Hong Kong
Purpose | Systematic energy assessment of the auditor's home (a shared student-hostel room) following the EMSD Code of Practice for Building Energy Audit (EAC 2018) and the EPD/EMSD GHG Guidelines for Buildings in Hong Kong: baseline consumption, consumption patterns, carbon inventory and Energy Management Opportunities.
Boundary | Household = Room 1003B (15 m², 2 occupants) + allocated shares of the shared washroom (4 users) and floor kitchen (32 residents) + the household's own hall-laundry use. Hall common services (lifts, corridors, central plant) are outside the boundary.
Period | Data collected 1 Jan - 11 Oct 2026; results expressed as a typical 12-month baseline year.
Colour legend | Blue text = input | Yellow fill = assumption | Black = formula | Green = link to another sheet
Key results (all live formulas)
Indicator | Value | Unit | Where calculated
Room AC energy (baseline, Octopus spend) | 810.8108 | kWh/yr | AC_Baseline
Room AC energy, bottom-up energy-label check | 884.4867 | kWh/yr | AC_Baseline
Household electricity (room + allocated shared services) | 2586.3877 | kWh/yr | Inventory
of which inside the 15 m² room | 1219.6108 | kWh/yr | Inventory
Electricity per person | 1293.1938 | kWh/person/yr | Inventory
Room EUI | 292.7066 | MJ/m²/yr | Monthly / Breakdown
Scope 1 (refrigerant screening) | 16.4375 | kg CO2e/yr | GHG_Inventory
Scope 2 - CLP-specific factor 0.34 | 879.3718 | kg CO2e/yr | GHG_Inventory
Scope 2 - territory default 0.7 | 1810.4714 | kg CO2e/yr | GHG_Inventory
Scope 3 (water, sewage, paper) | 43.3101 | kg CO2e/yr | GHG_Inventory
Household total (CLP basis) | 939.1194 | kg CO2e/yr | GHG_Inventory
Household total (default basis) | 1870.219 | kg CO2e/yr | GHG_Inventory
Per person (CLP basis) | 469.5597 | kg CO2e/person/yr | GHG_Inventory
Daily-activity extension (auditor) | 4601.4683 | kg CO2e/yr | Lifestyle_Scope3
Auditor's personal total | 5071.028 | kg CO2e/yr | Lifestyle_Scope3
Category I EMO saving (household) | 503.2179 | kWh/yr | EMO_Register
Category I EMO saving as % of household electricity | 19.46% | % | EMO_Register
Sheet guide
Inputs | All inputs with unit, data quality and source; HKO 1991-2020 monthly temperatures
AC_Baseline | Room AC: top-down (Octopus spend) vs bottom-up (HK energy label) reconciliation
HotWater | Monthly shower hot-water energy from first principles
Inventory | Equipment inventory with allocation of shared services (EAC Step 1-2)
Monthly | Monthly profile, monthly EUI and emissions
Breakdown | End-use and EAC-category breakdown, KPIs and HK benchmarks
GHG_Inventory | Scope 1-2-3 inventory in HK GHG Guidelines table format
Lifestyle_Scope3 | Auditor's commuting, flights and diet (reported separately)
EMO_Register | 18 EMOs by EAC category, with savings, costs, payback and CO2e
Sensitivity | One-at-a-time sensitivity of the key assumptions
EE-EAes_Summary | Executive summary in the structure of EMSD form EE-EAes
EE-EAes_Entry_Guide | Cell-by-cell values to type into the official macro-enabled EE-EAes form
Photo_Log | Evidence photographs and the data taken from each
Sources | Full references with URLs

## Inputs
Inputs & assumptions
Blue = input value; yellow fill = assumed typical value (flagged in the report); every formula in the workbook points here.
Name | Parameter | Value | Unit | Data quality | Source | Notes | Month | Days | Hot season (1 = May-Oct) | HKO mean air temp (°C)
Boundary & occupancy | [6 empty] | Jan | 31 | 0 | 16.5
OCC | Occupants of Room 1003B (household) | 2 | persons | Reported | S29 | Auditor + 1 roommate | Feb | 28 | 0 | 17.1
WR_USERS | Users of the shared washroom | 4 | persons | Reported | S29 | Shared by 4 residents | Mar | 31 | 0 | 19.4
KIT_USERS | Residents sharing the floor kitchen (allocation basis) | 32 | persons | Reported | S29 | ~20 use it actively; allocation is per resident with access | Apr | 30 | 0 | 23
OCC_WKDAY_H | Hours in room per weekday (22:00-11:00) | 13 | h/day | Reported | S29 | Q13 | May | 31 | 1 | 26.3
OCC_SAT_H | Hours in room on Saturday | 20 | h/day | Reported | S29 | Q14 | Jun | 30 | 1 | 28.3
OCC_SUN_H | Hours in room on Sunday | 18 | h/day | Reported | S29 | Q14 | Jul | 31 | 1 | 28.9
ROOM_AREA | Internal floor area of Room 1003B | 15 | m2 | Reported | S29 | Approximate, from hall information | Aug | 31 | 1 | 28.7
DAYS_HOT | Days in hot season (May-Oct) | 184 | days | Derived |  | 31+30+31+31+30+31 | Sep | 30 | 1 | 27.9
DAYS_COOL | Days in cool season (Nov-Apr) | 181 | days | Derived |  | 30+31+31+28+31+30 | Oct | 31 | 1 | 25.7
MJ_PER_KWH | Energy conversion | 3.6 | MJ/kWh | Published | S3 | Per EE-EAes Part 2 | Nov | 30 | 0 | 22.2
CP_WATER | Specific heat of water | 4.186 | kJ/kg.K | Published |  | Physical constant (1 L = 1 kg) | Dec | 31 | 0 | 18.2
Tariff & emission factors | [6 empty] | Year | 365 | 6 | 23.5493
TARIFF | Electricity price used to convert AC spend to kWh (proxy) | 1.406 | HK$/kWh | Published | S6 | CLP 2026 average net tariff; CityU's own Octopus AC rate not published - see Sensitivity | S8: HKO 1991-2020 normals (HKO HQ), day-weighted from 10-day & half-monthly normals; annual mean 23.5 °C.
TARIFF_LOW | Comparator hostel AC rate - low | 1.2 | HK$/kWh | Published | S25 | CUHK hostels
TARIFF_HIGH | Comparator hostel AC rate - high | 2.31 | HK$/kWh | Published | S25 | HKU JCSV IV
EF_CLP | CLP Power HK emission factor (2025, latest) | 0.34 | kg CO2e/kWh | Published | S5 | Power-company-specific factor (Guideline Table 5)
EF_CLP_PREV | CLP Power HK emission factor (2024) | 0.38 | kg CO2e/kWh | Published | S5 | For sensitivity
EF_DEFAULT | Territory-wide default electricity factor | 0.7 | kg CO2e/kWh | Published | S2 | Guideline Table 5 - must also be reported
WSD_FRESH | WSD unit electricity - fresh water | 0.624 | kWh/m3 | Published | S11 | x 0.7 kg/kWh per Guideline Table 8
WSD_SALT | WSD unit electricity - salt (flushing) water | 0.362 | kWh/m3 | Published | S11 | x 0.7 kg/kWh (optional item)
DSD_KWH | DSD unit electricity - sewage treated | 0.29 | kWh/m3 | Published | S12 | x 0.7 kg/kWh per Guideline Table 9
SEWER_FRAC | Fraction of fresh water entering sewer (residential) | 1 | - | Published | S2 | Guideline Table 9 note
PAPER_EF | Paper to landfill emission factor | 4.8 | kg CO2e/kg | Published | S2 | Guideline Table 7
GWP_R32 | GWP of HFC-32 (R32) | 650 | - | Published | S2 | Guideline Table 3-1
GWP_R410A | GWP of R-410A | 1725 | - | Published | S2 | Guideline Table 3-1
LEAK | Annual refrigerant leak rate (screening) | 0.04 | fraction/yr | Published | S21 | IPCC 2006 range 1-10%; 4% typical for developed economies
Room air-conditioner
AC_SPEND_HOT | Octopus AC spend - hot month (May-Oct), both occupants | 140 | HK$/month | Reported | S29 | Q18
AC_SPEND_COOL | Octopus AC spend - cool month (Nov-Apr), both occupants | 50 | HK$/month | Reported | S29 | Q18
AC_SPEND_STATED | Stated overall average AC spend | 120 | HK$/month | Reported | S29 | Initial answer - used as upper-bound scenario
AC_RATED_KW | Rated input power (cooling) | 1.192 | kW | Nameplate / label | S28 | Midea MW-12CRF8E
AC_CAP_KW | Rated cooling capacity | 3.34 | kW | Nameplate / label | S28 | 11,400 Btu/h
AC_CSPF | Cooling seasonal performance factor | 4.6618 | - | Nameplate / label | S28 | HK Energy Label Grade 1
AC_LABEL_KWH | Label annual energy consumption (cooling) | 362 | kWh/yr | Nameplate / label | S28 | Basis 1,200 h/yr
LABEL_HOURS | Operating hours behind HK label figure | 1200 | h/yr | Published | S9 | EMSD label basis
AC_H_HOT | AC operating hours - typical hot-season day | 12 | h/day | Reported | S29 | Q20 (on all night)
AC_H_COOL | AC operating hours - typical cool-season day | 4 | h/day | Reported | S29 | Q20
AC_SETPOINT | Usual set-point | 25 | degC | Reported | S29 | Q19
AC_CHARGE | Refrigerant charge (R32) - screening value | 0.4 | kg | Assumed |  | Typical for 1.5 HP R32 window unit; not on photographed label
DEG_SAVING | AC energy saving per +1 degC set-point | 0.03 | fraction | Published | S14 | HK Government figure
Room lighting & plug loads
CEIL_N | Ceiling LED linear battens | 2 | no. | Nameplate / label | S29 | Photo 05
CEIL_W | Power per ceiling batten | 20 | W | Assumed |  | Typical 1.2 m LED batten; no label visible
CEIL_H | Ceiling lights on | 6 | h/day | Reported | S29 | Q25
DESK_N | Under-shelf LED desk lights | 2 | no. | Reported | S29 | Q24
DESK_W | Power per desk light | 10 | W | Assumed |  | Typical 60 cm LED strip
DESK_H | Desk lights on | 4 | h/day | Assumed |  | Not reported
LAPTOP_W | Laptop adapter rating | 65 | W | Nameplate / label | S29 | HP TPN-CA17, Efficiency Level VI
LAPTOP_LF | Average laptop draw as fraction of adapter rating | 0.5 | - | Assumed |  | Adapter is sized for peak charging
LAPTOP_H | Laptop use | 8 | h/day | Reported | S29 | Q27
LAPTOP_N | Laptops in room (roommate assumed same as auditor) | 2 | no. | Assumed |  | Representative-occupant assumption
PHONE_W | Phone charger power | 20 | W | Assumed |  | Typical fast charger
PHONE_H | Phone charging | 1 | h/day | Reported | S29 | Q29
PHONE_N | Phones charged (both occupants) | 2 | no. | Assumed |  | Representative-occupant assumption
FAN_W | Desk fan rated power | 20 | W | Nameplate / label | S29 | ZW02-180, 220 V 50 Hz
FAN_H | Desk fan use | 12 | h/day | Reported | S29 | Q22
Shared washroom
SHOWERS | Showers per person per day | 1 | no./day | Reported | S29 | Q34
SHOWER_MIN | Shower duration | 5 | min | Reported | S29 | Q34
SHOWER_FLOW | Shower flow rate | 9 | L/min | Assumed |  | Typical modern showerhead; bucket test recommended
SHOWER_T | Delivered shower temperature | 40 | degC | Assumed |  | Typical comfortable shower
HEATER_EFF | Instantaneous heater efficiency | 0.99 | - | Assumed | S16 | Electronic instantaneous unit, negligible standing loss
HEATER_KW | Water heater rating at 380 V | 24.4 | kW | Published | S16 | Stiebel Eltron DHB-E 27
WR_FAN_W | Washroom exhaust fan power | 30 | W | Assumed |  | J.E.E. window-type exhaust fan; label not visible
WR_FAN_H | Exhaust fan running | 24 | h/day | Reported | S29 | Q35 - always on
WR_LIGHT_N | LED downlights | 3 | no. | Nameplate / label | S29 | Photos 08
WR_LIGHT_W | Power per downlight | 10 | W | Assumed |  | Typical LED downlight
WR_LIGHT_H | Sensor lights on | 3 | h/day | Reported | S29 | Q26
Shared kitchen
FRIDGE_N | Refrigerators | 2 | no. | Reported | S29 | Panasonic NR-BV361B, Grade 1
FRIDGE_KWH | Label consumption per refrigerator | 263 | kWh/yr | Nameplate / label | S29 | EMSD label U1-R230007/2023
DISP_KWH_DAY | Water dispenser standby + dispensing energy | 1.5 | kWh/day | Assumed | S20 | 3-temperature unit (10 L hot at 98 degC + ice); ENERGY STAR hot&cold limit 0.87
KAC_LABEL_KWH | Kitchen split AC label consumption | 688 | kWh/yr | Nameplate / label | S29 | Toshiba RAS-24J2KCV-HK, 7.00 kW, R410A
KAC_H_HOT | Kitchen AC running - hot season | 8 | h/day | Reported | S29 | Q46 - '8 hrs+, people don't turn it off'
KAC_H_COOL | Kitchen AC running - cool season | 4 | h/day | Assumed |  | Half of hot-season hours
KAC_CHARGE | Kitchen AC refrigerant charge (R410A) - screening | 1.4 | kg | Assumed |  | Typical 7 kW split
KLIGHT_N | Kitchen light fittings | 6 | no. | Assumed |  | Not photographed
KLIGHT_W | Power per kitchen fitting | 15 | W | Assumed |  | Typical LED
KLIGHT_H | Kitchen lights on | 16 | h/day | Assumed |  | Shared space in frequent use
COOK_SESS | Cooking sessions per person | 3 | per week | Reported | S29 | Q37
COOK_H | Induction hob on per session | 1 | h | Reported | S29 | Q37
COOK_KW | Average hob power while cooking | 1 | kW | Assumed |  | Philips HD4911 levels 400-2,100 W; mix of boil and simmer
Hall laundry
LAUNDRY_WK | Laundry loads per person | 1 | per week | Reported | S29 | Q39 (4 kg, 45 min wash)
WASH_KWH | Washer energy per cycle (cold wash) | 0.3 | kWh/cycle | Assumed |  | Motor + controls, no water heating
DRY_KW | Tumble-dryer heater + drum power | 3 | kW | Assumed |  | Typical electric dryer
DRY_MIN | Drying time per load | 12 | min | Reported | S29 | Q39
WASH_L | Water per wash | 60 | L/cycle | Assumed |  | Front-loader, part load
Water & paper
DRINK_L | Drinking water | 2 | L/person/day | Reported | S29 | Q40 (filtered, from dispenser)
OTHER_L | Basin, cooking & dish-washing water | 15 | L/person/day | Assumed |  | Typical
FLUSH_L | Toilet flushing (seawater) | 30 | L/person/day | Assumed | S13 | 5 flushes x 6 L; ~85% of HK uses seawater
SHEETS_SEM | Paper used per semester (50 printed + 50 written) | 100 | sheets | Reported | S29 | Q41
SEMS | Semesters per year | 2 | no. | Assumed
SHEET_G | Mass of one A4 80 g/m2 sheet | 5 | g | Derived |  | 0.0624 m2 x 80 g/m2
RECYCLE | Share of used paper recycled | 0.5 | fraction | Assumed | S29 | Auditor recycles; half assumed retained/landfilled
Daily-activity extension
COMMUTE_KM_WK | MTR commute distance (18 km x 2 x 6 days) | 216 | km/week | Reported | S29 | Q42
WEEKS | Weeks of commuting per year | 48 | weeks | Assumed | S29 | 52 less ~1 month break (Q15)
HOME_KM_MONTH | Other MTR trips (22 km x 2 x 3 per month) | 132 | km/month | Reported | S29 | Q43
MONTHS_IN_HK | Months per year in Hong Kong | 11 | months | Reported | S29 | Q15 - 1-month break
MTR_EF | MTR rail emission intensity | 0.0723 | kg CO2e/p-km | Published | S17 | MTR CDP 2022
FL_UPLIFT | Great-circle distance uplift | 1.08 | - | Published | S18 | DESNZ methodology (+8%)
EF_LONG | Long-haul economy, with RF | 0.11704 | kg CO2e/p-km | Published | S18 | DESNZ 2025
EF_SHORT | Short-haul economy, with RF | 0.1258 | kg CO2e/p-km | Published | S18 | DESNZ 2025 (derived: total incl. WTT 0.14825 less WTT 0.02249)
DIET_EF | Mixed (medium meat-eater) diet | 5.63 | kg CO2e/day | Published | S19 | Production emissions only
Benchmarks
BM_HH_KWH | Typical HK household electricity | 275 | kWh/month | Published | S7 | 3-person household
BM_HH_PERS | Persons in typical household | 3 | persons | Published | S7
BM_FLOOR_PP | Median per-capita floor area (2021 Census) | 16 | m2/person | Published | S23 | 172 sq ft
BM_WATER | HK domestic fresh water use | 120.9 | L/person/day | Published | S13 | 2023/24
BM_HK_T | HK per-capita GHG emissions (2023) | 4.58 | t CO2e/person | Published | S10 | Territorial inventory, AR5
BEC_LPD | BEC 2021 max lighting power density - dormitory | 6.2 | W/m2 | Published | S24

## AC_Baseline
Room air-conditioner baseline (Midea MW-12CRF8E, Octopus pre-paid)
Top-down = reported Octopus spend ÷ electricity price. Bottom-up = HK Energy Label average input power (362 kWh per 1,200 h) × reported operating hours.
Month | Days | Season | Octopus AC spend (HK$) | Top-down kWh (spend ÷ tariff) | AC operating hours (reported) | Bottom-up kWh (label kW × hours) | Scenario: stated HK$120/month (kWh) | Reconciliation & diagnostics | Value | Unit | Comment
Jan | 31 | Cool | 50 | 35.5619 | 124 | 37.4067 | 85.3485 | Label average input power (HK label basis) | 0.30167 | kW | 362 kWh / 1,200 h
Feb | 28 | Cool | 50 | 35.5619 | 112 | 33.7867 | 85.3485 | Rated input power (nameplate) | 1.192 | kW | Full-load inverter input
Mar | 31 | Cool | 50 | 35.5619 | 124 | 37.4067 | 85.3485 | Annual operating hours (reported pattern) | 2932 | h/yr | 12 h/day hot, 4 h/day cool
Apr | 30 | Cool | 50 | 35.5619 | 120 | 36.2 | 85.3485 | BASELINE: top-down annual AC energy | 810.8108 | kWh/yr | Used in the inventory
May | 31 | Hot | 140 | 99.5733 | 372 | 112.22 | 85.3485 | Bottom-up annual AC energy (label method) | 884.4867 | kWh/yr | Independent physical check
Jun | 30 | Hot | 140 | 99.5733 | 360 | 108.6 | 85.3485 | Difference, bottom-up vs top-down | 9.087% | % | Within ±10% = good agreement
Jul | 31 | Hot | 140 | 99.5733 | 372 | 112.22 | 85.3485 | Upper-bound scenario (stated HK$120 × 12) | 1024.1821 | kWh/yr | Not reconciled with seasonal answers
Aug | 31 | Hot | 140 | 99.5733 | 372 | 112.22 | 85.3485 | Implied Octopus rate if bottom-up is right | 1.2889 | HK$/kWh | Cf. CUHK 1.20 - HKU 2.31 (S25)
Sep | 30 | Hot | 140 | 99.5733 | 360 | 108.6 | 85.3485 | Average input power while running (top-down) | 0.27654 | kW | Inverter part-load operation
Oct | 31 | Hot | 140 | 99.5733 | 372 | 112.22 | 85.3485 | Equivalent full-load hours at rated input | 680.2104 | h/yr
Nov | 30 | Cool | 50 | 35.5619 | 120 | 36.2 | 85.3485 | Hot-season (May-Oct) AC energy | 597.4395 | kWh/yr
Dec | 31 | Cool | 50 | 35.5619 | 124 | 37.4067 | 85.3485 | Hot-season share of AC energy | 73.68% | %
Year | 365 |  | 1140 | 810.8108 | 2932 | 884.4867 | 1024.1821 | Cool-season (Nov-Apr) AC energy | 213.3713 | kWh/yr
[8 empty] | Annual AC spend (both occupants) | 1140 | HK$/yr | HK$570 per person
[8 empty] | Approx. cooling delivered (top-down × label CSPF) | 3779.8378 | kWh(th)/yr | Seasonal efficiency basis

## HotWater
Shower hot water - Stiebel Eltron DHB-E 27 instantaneous heater (shared washroom)
Energy = litres × 4.186 kJ/kg.K × (40 °C - cold-water inlet) ÷ 3,600 ÷ efficiency. Inlet temperature taken as the HKO monthly mean air temperature (assumption).
Month | Days | Cold-water inlet ≈ HKO mean (°C) | Temperature rise to 40 °C (K) | Shower water per person (L/day) | Heater energy per person (kWh/day) | Household heater energy (kWh/month) | Heater power needed at full flow (kW) | Diagnostics | Value | Unit
Jan | 31 | 16.5 | 23.5 | 45 | 1.2421 | 77.0076 | 14.9047 | Heater rating at 380 V (DHB-E 27) | 24.4 | kW
Feb | 28 | 17.1 | 22.9 | 45 | 1.2103 | 67.7794 | 14.5242 | Peak power needed for one shower (January) | 14.9047 | kW
Mar | 31 | 19.4 | 20.6 | 45 | 1.0888 | 67.5045 | 13.0654 | Capacity headroom (rating ÷ need) | 1.6371 | ×
Apr | 30 | 23 | 17 | 45 | 0.89851 | 53.9106 | 10.7821 | Household shower energy | 634.7181 | kWh/yr
May | 31 | 26.3 | 13.7 | 45 | 0.72409 | 44.8938 | 8.6891 | Per person | 317.3591 | kWh/yr
Jun | 30 | 28.3 | 11.7 | 45 | 0.61839 | 37.1032 | 7.4206 | Shower water per person | 16.425 | m3/yr
Jul | 31 | 28.9 | 11.1 | 45 | 0.58667 | 36.3738 | 7.0401 | January vs July daily energy | 2.1171 | ×
Aug | 31 | 28.7 | 11.3 | 45 | 0.59724 | 37.0292 | 7.1669
Sep | 30 | 27.9 | 12.1 | 45 | 0.63953 | 38.3717 | 7.6743
Oct | 31 | 25.7 | 14.3 | 45 | 0.75581 | 46.8599 | 9.0697
Nov | 30 | 22.2 | 17.8 | 45 | 0.94079 | 56.4476 | 11.2895
Dec | 31 | 18.2 | 21.8 | 45 | 1.1522 | 71.4368 | 13.8265
Year | 365 | 23.5493 | 16.4507 | 45 | 0.86948 | 634.7181 | 14.9047

## Inventory
Equipment inventory and annual energy (EAC 2018 Step 1-2)
Household = Room 1003B (2 occupants). Room loads count in full; shared washroom fixed loads at 2/4; shared kitchen fixed loads at 2/32; usage-based items (showers, cooking, laundry) at the household's own use.
ID | Space | Item | Make / model / evidence | Power basis (W) | Qty | Use (h/day) or basis | Item annual kWh | Household share | Household kWh/yr | Per person kWh/yr | End-use | EAC 8.1(g)(iv) category | Data quality | Photo / note
R1 | Room | Window air-conditioner | Midea MW-12CRF8E, 1.5 HP inverter, R32, Grade 1 | 1192 | 1 | Octopus spend ÷ tariff | 810.8108 | 1 | 810.8108 | 405.4054 | Air-conditioning | Air-conditioning | Reported spend + label | 03a, 03b
R2 | Room | Ceiling LED linear battens | 2 surface battens (no label visible) | 20 | 2 | 6 | 87.6 | 1 | 87.6 | 43.8 | Lighting | Lighting | Assumed W, reported h | 05a
R3 | Room | Under-shelf LED desk lights | Integrated in furniture | 10 | 2 | 4 | 29.2 | 1 | 29.2 | 14.6 | Lighting | Lighting | Assumed | 05b
R4 | Room | Oscillating desk fan | ZW02-180, 20 W nameplate | 20 | 1 | 12 | 87.6 | 1 | 87.6 | 43.8 | Air movement (fan) | Air-conditioning | Nameplate + reported | 06b
R5 | Room | Laptops (auditor + roommate) | HP 65 W adapter TPN-CA17 (avg draw 50%) | 32.5 | 2 | 8 | 189.8 | 1 | 189.8 | 94.9 | Plug loads | Others | Nameplate + assumed LF | 06a
R6 | Room | Phone chargers | Typical 20 W fast charger | 20 | 2 | 1 | 14.6 | 1 | 14.6 | 7.3 | Plug loads | Others | Assumed W, reported h | -
W1 | Washroom | Instantaneous water heater (household showers) | Stiebel Eltron DHB-E 27, 24.4 kW @380 V | 24400 | 1 | See HotWater sheet | 634.7181 | 1 | 634.7181 | 317.3591 | Hot water | Others | Physics model | 08a, 08e
W2 | Washroom | Window exhaust fan (runs 24 h) | J.E.E. window fan (label not visible) | 30 | 1 | 24 | 262.8 | 0.5 | 131.4 | 65.7 | Ventilation | Air-conditioning | Assumed W, reported h | 08c, 08d
W3 | Washroom | LED downlights (occupancy sensor) | 3 surface downlights | 10 | 3 | 3 | 32.85 | 0.5 | 16.425 | 8.2125 | Lighting | Lighting | Assumed W, reported h | 08b
K1 | Kitchen | Refrigerators | Panasonic NR-BV361B, Grade 1, 263 kWh/yr label |  | 2 | Energy label | 526 | 0.0625 | 32.875 | 16.4375 | Refrigeration | Others | Energy label | 09i
K2 | Kitchen | 3-temperature water dispenser | Aquatek AQ-1323T, 750 W heater + 160 W compressor | 910 | 1 | 1.5 kWh/day (assumed) | 547.5 | 0.0625 | 34.2188 | 17.1094 | Drinking water | Others | Assumed | 09a, 09b
K3 | Kitchen | Split air-conditioner | Toshiba RAS-24J2KCV-HK, 7.0 kW, R410A, Grade 1 (688 kWh/1,200 h) | 573.3333 | 1 | 8 h/day hot, 4 h/day cool | 1259.04 | 0.0625 | 78.69 | 39.345 | Air-conditioning | Air-conditioning | Label + observed | 09f, 09g
K4 | Kitchen | Kitchen lighting | Not photographed | 15 | 6 | 16 | 525.6 | 0.0625 | 32.85 | 16.425 | Lighting | Lighting | Assumed | -
K5 | Kitchen | Induction cooking (household) | Philips HD4911/80, 2,100 W max, Grade 2 (88.1%) | 1000 | 2 | 0.42857 | 312 | 1 | 312 | 156 | Cooking | Others | Reported use + assumed kW | 09c-09e
L1 | Laundry | Washing machine (household) | Hall machine, cold wash 45 min |  | 2 | 1 load/week each | 31.2 | 1 | 31.2 | 15.6 | Laundry | Others | Reported use + assumed kWh | -
L2 | Laundry | Tumble dryer (household) | Hall machine, 12 min per load | 3000 | 2 | 12 min/load | 62.4 | 1 | 62.4 | 31.2 | Laundry | Others | Reported use + assumed kW | -
Total | [8 empty] | 2586.3877 | 1293.1938
|  | Space | Household kWh/yr | % of household | Per person kWh/yr
|  | Room 1003B (15 m²) | 1219.6108 | 47.15% | 609.8054
|  | Shared washroom | 782.5431 | 30.26% | 391.2716
|  | Shared kitchen | 490.6338 | 18.97% | 245.3169
|  | Hall laundry | 93.6 | 3.619% | 46.8
|  | Total household | 2586.3877 | 100% | 1293.1938
|  | Outside the room (shared / usage-based) | 1366.7769 | 52.85%
|  | Check: space total - inventory total (must be 0) | 0

## Monthly
Monthly energy, EUI and emissions profile (typical baseline year)
Feeds EAC 2018 §8.1(g)(iii) monthly EUI and EE-EAes Part 2 item 5. Room-only = loads inside the 15 m² room.
Month | Days | Season | Room AC | Desk fan | Room lighting | Room plug loads | Hot water | Washroom fan + lights (share) | Kitchen AC (share) | Kitchen fridges, dispenser, lights (share) | Cooking | Laundry | Household total kWh | Household total MJ | Room-only kWh | Room EUI (MJ/m²) | Per person kWh | kg CO2e (CLP 0.34) | kg CO2e (default 0.7)
Jan | 31 | Cool | 35.5619 | 7.44 | 9.92 | 17.36 | 77.0076 | 12.555 | 4.4433 | 8.4884 | 26.4986 | 7.9496 | 207.2244 | 746.0079 | 70.2819 | 16.8677 | 103.6122 | 70.4563 | 145.0571
Feb | 28 | Cool | 35.5619 | 6.72 | 8.96 | 15.68 | 67.7794 | 11.34 | 4.0133 | 7.6669 | 23.9342 | 7.1803 | 188.836 | 679.8097 | 66.9219 | 16.0613 | 94.418 | 64.2042 | 132.1852
Mar | 31 | Cool | 35.5619 | 7.44 | 9.92 | 17.36 | 67.5045 | 12.555 | 4.4433 | 8.4884 | 26.4986 | 7.9496 | 197.7213 | 711.7968 | 70.2819 | 16.8677 | 98.8607 | 67.2253 | 138.4049
Apr | 30 | Cool | 35.5619 | 7.2 | 9.6 | 16.8 | 53.9106 | 12.15 | 4.3 | 8.2146 | 25.6438 | 7.6932 | 181.074 | 651.8665 | 69.1619 | 16.5989 | 90.537 | 61.5652 | 126.7518
May | 31 | Hot | 99.5733 | 7.44 | 9.92 | 17.36 | 44.8938 | 12.555 | 8.8867 | 8.4884 | 26.4986 | 7.9496 | 243.5653 | 876.8351 | 134.2933 | 32.2304 | 121.7827 | 82.8122 | 170.4957
Jun | 30 | Hot | 99.5733 | 7.2 | 9.6 | 16.8 | 37.1032 | 12.15 | 8.6 | 8.2146 | 25.6438 | 7.6932 | 232.578 | 837.2807 | 133.1733 | 31.9616 | 116.289 | 79.0765 | 162.8046
Jul | 31 | Hot | 99.5733 | 7.44 | 9.92 | 17.36 | 36.3738 | 12.555 | 8.8867 | 8.4884 | 26.4986 | 7.9496 | 235.0453 | 846.1632 | 134.2933 | 32.2304 | 117.5227 | 79.9154 | 164.5317
Aug | 31 | Hot | 99.5733 | 7.44 | 9.92 | 17.36 | 37.0292 | 12.555 | 8.8867 | 8.4884 | 26.4986 | 7.9496 | 235.7007 | 848.5225 | 134.2933 | 32.2304 | 117.8504 | 80.1382 | 164.9905
Sep | 30 | Hot | 99.5733 | 7.2 | 9.6 | 16.8 | 38.3717 | 12.15 | 8.6 | 8.2146 | 25.6438 | 7.6932 | 233.8465 | 841.8473 | 133.1733 | 31.9616 | 116.9232 | 79.5078 | 163.6925
Oct | 31 | Hot | 99.5733 | 7.44 | 9.92 | 17.36 | 46.8599 | 12.555 | 8.8867 | 8.4884 | 26.4986 | 7.9496 | 245.5315 | 883.9133 | 134.2933 | 32.2304 | 122.7657 | 83.4807 | 171.872
Nov | 30 | Cool | 35.5619 | 7.2 | 9.6 | 16.8 | 56.4476 | 12.15 | 4.3 | 8.2146 | 25.6438 | 7.6932 | 183.611 | 660.9996 | 69.1619 | 16.5989 | 91.8055 | 62.4277 | 128.5277
Dec | 31 | Cool | 35.5619 | 7.44 | 9.92 | 17.36 | 71.4368 | 12.555 | 4.4433 | 8.4884 | 26.4986 | 7.9496 | 201.6536 | 725.9531 | 70.2819 | 16.8677 | 100.8268 | 68.5622 | 141.1575
Year | 365 |  | 810.8108 | 87.6 | 116.8 | 204.4 | 634.7181 | 147.825 | 78.69 | 99.9437 | 312 | 93.6 | 2586.3877 | 9310.9956 | 1219.6108 | 292.7066 | 1293.1938 | 879.3718 | 1810.4714
Check: monthly total - inventory total (must be 0) | [12 empty] | 0
Check: room-only total - room inventory (must be 0) | [14 empty] | 0

## Breakdown
Energy breakdown, EUI and benchmarks
EAC 2018 §8.1(g)(ii)-(iv): EUI, monthly EUI and percentage breakdown by installation.
A. End-use breakdown - household (Room 1003B + allocated shared services)
End-use | kWh/yr | % of total | kWh/person/yr | kg CO2e/yr (CLP) | kg CO2e/yr (default 0.7)
Air-conditioning | 889.5008 | 34.39% | 444.7504 | 302.4303 | 622.6506
Hot water | 634.7181 | 24.54% | 317.3591 | 215.8042 | 444.3027
Cooking | 312 | 12.06% | 156 | 106.08 | 218.4
Plug loads | 204.4 | 7.903% | 102.2 | 69.496 | 143.08
Lighting | 166.075 | 6.421% | 83.0375 | 56.4655 | 116.2525
Ventilation | 131.4 | 5.08% | 65.7 | 44.676 | 91.98
Air movement (fan) | 87.6 | 3.387% | 43.8 | 29.784 | 61.32
Laundry | 93.6 | 3.619% | 46.8 | 31.824 | 65.52
Drinking water | 34.2188 | 1.323% | 17.1094 | 11.6344 | 23.9531
Refrigeration | 32.875 | 1.271% | 16.4375 | 11.1775 | 23.0125
Total | 2586.3877 | 100% | 1293.1938 | 879.3718 | 1810.4714
B. EAC 2018 §8.1(g)(iv) categories
Category | Room 1003B kWh/yr | % (room) | Household kWh/yr | % (household) | Room MJ/yr
Air-conditioning | 898.4108 | 73.66% | 1108.5008 | 42.86% | 3234.2789
Lighting | 116.8 | 9.577% | 166.075 | 6.421% | 420.48
Others | 204.4 | 16.76% | 1311.8119 | 50.72% | 735.84
Lift & escalator | 0 | 0% | 0 | 0% | 0
Total | 1219.6108 | 100% | 2586.3877 | 100% | 4390.5989
Lift & escalator: not applicable to the audited unit (hall lifts are outside the household boundary).
C. Key performance indicators and Hong Kong benchmarks
Indicator | Value | Unit | Benchmark | Benchmark basis | Ratio to benchmark
Room EUI (energy inside the 15 m² room) | 81.3074 | kWh/m²/yr | 68.75 | Typical HK home: 275 kWh/month ÷ 3 persons ÷ 16 m²/person (S7, S23) | 1.1827
Room EUI | 292.7066 | MJ/m²/yr | 247.5 | As above, in MJ | 1.1827
Household electricity per person | 1293.1938 | kWh/person/yr | 1100 | Typical HK household (S7) | 1.1756
Share of household energy used outside the room | 52.85% | % |  | Shared washroom, kitchen, laundry
Room lighting power density | 4 | W/m² | 6.2 | BEC 2021 max LPD, dormitory (S24) | 0.64516
Floor area per occupant | 7.5 | m²/person | 16 | Median HK per-capita floor area (S23) | 0.46875
Fresh water use per person | 70.5714 | L/person/day | 120.9 | HK domestic fresh water 2023/24 (S13) | 0.58372
AC share of room energy | 73.66% | % |  | Incl. desk fan
Hot water share of household energy | 24.54% | %

## GHG_Inventory
Greenhouse gas inventory - HK GHG Guidelines for Buildings (EPD/EMSD 2010) format
Reporting entity: household of Room 1003B (2 occupants). Physical boundary: the room plus allocated shares of the shared washroom and kitchen, and the household's hall-laundry use. Baseline year: typical 12 months (data Jan-Oct 2026).
SCOPE 1 - Direct emissions
Table 1 - Stationary combustion
Source | Fuel | Amount | Unit | CO2e factor | kg CO2e/yr
Cooking and water heating | None - all-electric (induction hob, electric heater) | 0 | - | 0 | 0
Table 3 - HFC refrigerant (mass-balance method: inventory change)
Equipment | Refrigerant | Cs (kg) | Ci (kg) | Cd (kg) | Ce (kg) | GWP | kg CO2e/yr
Room window AC | R32 (HFC-32) | 0 | 0 | 0 | 0 | 650 | 0
Kitchen split AC | R-410A | 0 | 0 | 0 | 0 | 1725 | 0
Occupants hold, buy and dispose of no refrigerant, so the Guideline mass-balance gives zero. A leak-rate screening estimate is added below so fugitive HFCs are not omitted.
Screening estimate - IPCC 2006 operating leak rate (included in Scope 1)
Equipment | Refrigerant | Charge (kg) | Leak rate /yr | GWP | Household share | kg CO2e/yr
Room window AC | R32 | 0.4 | 4% | 650 | 1 | 10.4
Kitchen split AC | R-410A | 1.4 | 4% | 1725 | 0.0625 | 6.0375
Scope 1 total | [5 empty] | 16.4375
SCOPE 2 - Energy indirect emissions (Table 5: purchased electricity, CLP Power)
Facility / source | Electricity (kWh/yr) | CLP-specific factor (kg/kWh) | Territory default (kg/kWh) | kg CO2e/yr (CLP) | kg CO2e/yr (default)
Room 1003B (incl. Octopus-metered AC) | 1219.6108 | 0.34 | 0.7 | 414.6677 | 853.7276
Shared washroom (own showers + 2/4 of fan & lights) | 782.5431 | 0.34 | 0.7 | 266.0647 | 547.7802
Shared kitchen (own cooking + 2/32 of fixed loads) | 490.6338 | 0.34 | 0.7 | 166.8155 | 343.4436
Hall laundry (own use) | 93.6 | 0.34 | 0.7 | 31.824 | 65.52
Scope 2 total | 2586.3877 |  |  | 879.3718 | 1810.4714
Table 6 - Towngas: not applicable (no Towngas or LPG used).
SCOPE 3 - Other indirect emissions (optional under the Guidelines)
Quantity | Value | Unit | Basis
Shower water | 45 | L/person/day | HotWater sheet
Drinking water (dispenser) | 2 | L/person/day | Reported
Basin, cooking and dish-washing | 15 | L/person/day | Assumed
Laundry water | 8.5714 | L/person/day | 60 L per weekly load
Paper purchased (Pi) | 2 | kg/yr (household) | 100 sheets/semester each
Paper recycled (Pr) | 1 | kg/yr | Half recycled (assumed)
Paper in storage at start / end (Ps, Pe) | 0 | kg | Negligible
Fresh water per person | 70.5714 | L/person/day
Household fresh water | 51.5171 | m3/yr
Household seawater (toilet flushing) | 21.9 | m3/yr | 5 flushes x 6 L/person/day
Guideline item | Quantity | Unit | Emission factor | Factor unit | kg CO2e/yr | Factor basis
Table 7 - Paper waste to landfill | 1 | kg | 4.8 | kg CO2e/kg | 4.8 | Guideline default 4.8
Table 8 - Fresh water (WSD) | 51.5171 | m3 | 0.4368 | kg CO2e/m3 | 22.5027 | 0.624 kWh/m3 × 0.7
Table 9 - Sewage (DSD) | 51.5171 | m3 | 0.203 | kg CO2e/m3 | 10.458 | 0.29 kWh/m3 × 0.7
Seawater for flushing (WSD, optional) | 21.9 | m3 | 0.2534 | kg CO2e/m3 | 5.5495 | 0.362 kWh/m3 × 0.7
Scope 3 total |  |  |  |  | 43.3101
SUMMARY - household (Room 1003B, 2 occupants)
Scope | kg CO2e/yr (CLP-specific) | kg CO2e/yr (territory default) | t CO2e/yr (CLP) | % of total (CLP) | kg CO2e/person/yr (CLP) | kg CO2e/person/yr (default)
Scope 1 - direct (refrigerant screening) | 16.4375 | 16.4375 | 0.016438 | 1.75% | 8.2188 | 8.2188
Scope 2 - purchased electricity | 879.3718 | 1810.4714 | 0.87937 | 93.64% | 439.6859 | 905.2357
Scope 3 - water, sewage, paper | 43.3101 | 43.3101 | 0.04331 | 4.612% | 21.6551 | 21.6551
TOTAL | 939.1194 | 1870.219 | 0.93912 | 100% | 469.5597 | 935.1095
Emission intensity of the room (Scope 2, CLP basis) | 27.6445 | kg CO2e/m²/yr

## Lifestyle_Scope3
Daily-activity extension - the auditor's personal Scope 3 footprint
Reported separately from the building inventory (GHG Protocol / ISO 14064-1 Scope 3 categories). Per auditor only, not per household.
Activity | Quantity | Unit | Emission factor | Factor unit | kg CO2e/yr | Basis
MTR commute (18 km x 2 x 6 days/week) | 10368 | p-km | 0.0723 | kg CO2e/p-km | 749.6064 | MTR CDP 2022 (S17); 48 weeks
Other MTR trips (22 km x 2 x 3/month) | 1452 | p-km | 0.0723 | kg CO2e/p-km | 104.9796 | 11 months in HK
Flights (4 legs, table below) | 14334.516 | p-km | 0.11803 | kg CO2e/p-km | 1691.9323 | DESNZ 2025 economy incl. RF (S18)
Diet - mixed (medium meat-eater) | 365 | days | 5.63 | kg CO2e/day | 2054.95 | Scarborough et al. 2014 (S19)
Lifestyle total |  |  |  |  | 4601.4683
Flight leg | Great-circle km | Haul | Distance incl. 8% uplift (km) | Factor (kg CO2e/p-km) | kg CO2e
Hong Kong (HKG) - Delhi (DEL) | 3747 | Long-haul | 4046.76 | 0.11704 | 473.6328
Delhi (DEL) - Hong Kong (HKG) | 3747 | Long-haul | 4046.76 | 0.11704 | 473.6328
Delhi (DEL) - Goa (GOI) | 1503.1 | Short-haul | 1623.348 | 0.1258 | 204.2172
Goa (GOI) - Hong Kong (HKG) | 4275.6 | Long-haul | 4617.648 | 0.11704 | 540.4495
Flights total | 13272.7 |  | 14334.516 |  | 1691.9323
Personal footprint (auditor) | kg CO2e/yr | % of personal total
Home energy & water (household inventory ÷ 2) | 469.5597 | 9.26%
MTR travel | 854.586 | 16.85%
Flights | 1691.9323 | 33.36%
Diet | 2054.95 | 40.52%
Personal total | 5071.028 | 100%
HK per-capita emissions 2023 (territorial, S10) | 4580
Ratio: personal total / HK per-capita (different scope - see report) | 1.1072

## EMO_Register
Energy Management Opportunities (EAC 2018 §6.2 categories; EE-EAes Part 3 types)
Cat I = housekeeping, no cost; Cat II = low-cost operational changes; Cat III = higher capital cost. Types: LG lighting, AC air-conditioning, EL electrical, LE lift/escalator, Others. Capital costs are indicative and must be confirmed by quotation.
Ref | Cat. | Type | Responsible party | Energy management opportunity | Basis of saving estimate | Facility saving (kWh/yr) | Household share (kWh/yr) | Household saving (HK$/yr) | Indicative capital cost (HK$) | Simple payback (yr) | Service life (yr) | Facility saving (kg CO2e/yr) | Household saving (kg CO2e/yr) | Recommendation
EMO-01 | I | AC | Occupants | Raise the AC set-point from 25 °C to 26 °C and keep the 20 W desk fan running for air movement | 3% of AC energy per +1 °C (S14) | 24.3243 | 24.3243 | 34.2 | 0 | 0 | - | 8.2703 | 8.2703 | Implement now
EMO-02 | I | AC | Occupants | Use the AC's built-in timer to switch off 2 h before waking in hot months (12 to 10 h/day) | 2/12 of hot-season AC energy | 99.5733 | 99.5733 | 140 | 0 | 0 | - | 33.8549 | 33.8549 | Implement now
EMO-03 | I | AC | Occupants | Clean the AC filter fortnightly in summer, wipe the soiled louvres, close the curtain against late-afternoon NW sun | 5% of AC energy (S26, S32) | 40.5405 | 40.5405 | 57 | 0 | 0 | - | 13.7838 | 13.7838 | Implement now
EMO-04 | I | LG | Occupants | Use the desk task lights instead of both ceiling battens for 3 of the 6 lit hours | 2 x 20 W x 3 h/day avoided | 43.8 | 43.8 | 61.5828 | 0 | 0 | - | 14.892 | 14.892 | Implement now
EMO-05 | I | Others | Occupants | Shorten showers from 5 to 4 minutes | 20% of shower heating energy | 126.9436 | 126.9436 | 178.4827 | 0 | 0 | - | 43.1608 | 43.1608 | Implement now
EMO-06 | I | Others | Occupants | Lower the delivered shower temperature from 40 °C to 38 °C (turn the heater dial down) | 2 K of the annual-average temperature rise | 77.1662 | 77.1662 | 108.4956 | 0 | 0 | - | 26.2365 | 26.2365 | Implement now
EMO-07 | I | EL | Occupants | Laptop power management: lower brightness, sleep after 10 min idle, battery-saver mode | 15% of laptop energy (assumed) | 28.47 | 28.47 | 40.0288 | 0 | 0 | - | 9.6798 | 9.6798 | Implement now
EMO-08 | I | Others | Occupants | Cook with lids, match pan to the induction zone, batch-cook two meals per session | 20% of cooking energy (assumed) | 62.4 | 62.4 | 87.7344 | 0 | 0 | - | 21.216 | 21.216 | Implement now
EMO-09 | II | AC | Hall (Student Residence Office) | Washroom exhaust fan: replace 24 h running with an occupancy / humidistat run-on control (~8 h/day) | 16 of 24 fan-hours avoided | 175.2 | 87.6 | 123.1656 | 800 | 3.2477 | 10 | 59.568 | 29.784 | Recommend to hall
EMO-10 | II | AC | Hall (Student Residence Office) | Kitchen AC: 7-day timer + occupancy interlock, set-point locked at 25.5 °C (8 to 5 h/day hot, 4 to 2 h/day cool) | Label 0.573 kW x hours avoided | 524.0267 | 32.7517 | 46.0488 | 1000 | 1.3573 | 10 | 178.1691 | 11.1356 | Recommend to hall
EMO-11 | II | Others | Hall (Student Residence Office) | Water dispenser: enable night set-back / timer on hot and ice tanks (00:00-06:00) | 25% of dispenser energy (assumed) | 136.875 | 8.5547 | 12.0279 | 200 | 1.0393 | 10 | 46.5375 | 2.9086 | Recommend to hall
EMO-12 | II | Others | Hall (Student Residence Office) | Fit a WELS Grade-1 low-flow showerhead (9 to 7 L/min) in the shared washroom | 22% of shower energy and water, 4 users | 282.0969 | 141.0485 | 198.3141 | 250 | 0.63031 | 5 | 95.913 | 47.9565 | Recommend to hall
EMO-13 | II | AC | Hall (Student Residence Office) | Annual professional clean of the window-AC coil and louvres (heavy soiling seen in photo 03b) | 3% of AC energy (S26) | 24.3243 | 24.3243 | 34.2 | 400 | 11.6959 | 1 | 8.2703 | 8.2703 | Recommend on hygiene grounds; bundle with routine maintenance (EAC 7.6.4)
EMO-14 | II | EL | Occupants | Buy a plug-in power meter (about HK$120) to measure the laptop, fan and AC and verify savings (EAC §7.6.3) | Enabling measure - no saving claimed | 0 | 0 | 0 | 120 | n/a | 5 | 0 | 0 | Implement now (within HK$200 budget)
EMO-15 | III | Others | Hall (CityU) | Replace 24.4 kW instantaneous shower heaters with central air-source heat-pump water heating (COP about 3.5) and storage | Electricity x (1 - 0.99/3.5), 4 users | 910.3671 | 455.1836 | 639.9881 | 20000 | 15.6253 | 15 | 309.5248 | 154.7624 | Further study (also cuts peak demand)
EMO-16 | III | AC | Hall (CityU) | Replace the Grade-1 window AC (CSPF 4.66) with a best-in-class split unit (CSPF about 7.5) | AC x (1 - 4.66/7.5) | 306.8324 | 306.8324 | 431.4064 | 9000 | 20.862 | 12 | 104.323 | 104.323 | Not viable - payback exceeds service life
EMO-17 | III | AC | Hall (CityU) | Solar-control film on the NW single glazing (1.55 m²) | 2% of AC energy (assumed) | 16.2162 | 16.2162 | 22.8 | 800 | 35.0877 | 10 | 5.5135 | 5.5135 | Not viable at present
EMO-18 | III | Others | Hall (CityU) | Expand rooftop solar PV under the CLP Feed-in Tariff (the village already has 110 panels) | Renewable-energy viability statement (EAC §7.4.4(d)) | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | Further study by CityU
Category | No. of EMOs | Household saving (kWh/yr) | % of household electricity | Household saving (kg CO2e/yr) | Facility saving (kWh/yr)
Category I | 8 | 503.2179 | 19.46% | 171.0941 | 503.2179
Category II | 6 | 294.2791 | 11.38% | 100.0549 | 1142.5229
Category III | 4 | 778.2322 | 30.09% | 264.5989 | 1233.4158
All EMOs (indicative - savings interact, not fully additive) | 18 | 1575.7293 | 60.92% | 535.7479 | 2879.1566
EE-EAes type | No. of EMOs
Lighting (LG) | 1
Air-conditioning (AC) | 8
Electrical (EL) | 2
Lift/Escalator (LE) | 0
Others | 7

## Sensitivity
Sensitivity analysis - which assumptions matter?
Each scenario changes one input and recomputes the household total; Scope 2 uses the CLP factor unless the scenario changes the factor.
# | Scenario | Value tested | Room AC (kWh/yr) | Household electricity (kWh/yr) | Household Scope 2 (kg CO2e/yr) | Change vs base
0 | Base case | CLP 0.34; HK$1.406/kWh | 810.8108 | 2586.3877 | 879.3718 | 0%
1 | CLP 2024 emission factor | 0.38 | 810.8108 | 2586.3877 | 982.8273 | 11.76%
2 | Territory-wide default factor | 0.7 | 810.8108 | 2586.3877 | 1810.4714 | 105.9%
3 | Octopus AC rate HK$1.20/kWh (CUHK level) | 1.2 | 950 | 2725.5769 | 926.6961 | 5.382%
4 | Octopus AC rate HK$2.31/kWh (HKU level) | 2.31 | 493.5065 | 2269.0833 | 771.4883 | -12.27%
5 | Stated flat average HK$120/month | 120 | 1024.1821 | 2799.7589 | 951.918 | 8.25%
6 | Bottom-up AC (label 362 kWh/1,200 h) | 362 | 884.4867 | 2660.0635 | 904.4216 | 2.849%
7 | Shower flow 7 L/min (Grade-1 head) | 7 | 810.8108 | 2445.3392 | 831.4153 | -5.453%
8 | Shower flow 12 L/min | 12 | 810.8108 | 2797.9604 | 951.3065 | 8.18%
9 | Laptop average draw 30% of adapter | 0.3 | 810.8108 | 2510.4677 | 853.559 | -2.935%
10 | Laptop average draw 80% of adapter | 0.8 | 810.8108 | 2700.2677 | 918.091 | 4.403%
11 | Roommate uses half the auditor's personal loads | 0.5 | 810.8108 | 2275.2081 | 773.5708 | -12.03%
12 | Kitchen allocated over 20 active users (not 32) | 20 | 810.8108 | 2693.5679 | 915.8131 | 4.144%
13 | One month away (11 of 12 months occupied) | 0.91667 | 743.2432 | 2398.0603 | 815.3405 | -7.281%

## EE-EAes_Summary
Executive Summary - adapted from EMSD Technical Form EE-EAes (V.2)
Residential buildings are not prescribed under Cap. 610; the form's structure is applied voluntarily to the audited home. Values link to the calculation sheets.
Part 1 - (A) Administrative information (EAC Clause 8.1(m))
Name of building (entity audited) | Hall 13, CityU Lee Shau Kee Student Residence Village - Room 1003B, 10/F
Address of building | Ma On Shan, New Territories, Hong Kong
1) Date of commencement of energy audit | 01/01/2026
2) Date of completion of energy audit | 11/10/2026
3) Energy Audit Form validity | N/A - voluntary home audit (not issued under Cap. 610)
4) Energy Audit Report reference no. | SEE8115-HEA-2026-01
5) Energy imported from / exported to other buildings? | No. The room is supplied from the hall's CLP supply; room AC is pre-paid by Octopus card.
Part 1 - (B)(I) Building type, usage and operation
1)(a) Type of building | Others - residential student hostel (MiC, 2024)
1)(b) Portion of common area | N/A - audited unit is a single room; shared washroom and kitchen allocated by users
1)(c) No. of blocks | Village of 3 towers / 6 halls (S15); audited unit in Hall 13
2) Internal floor area of audited unit (m²) | 15
3) Floor of audited unit | 10/F
4) Major type of facade | MiC concrete modules; dark aluminium-framed single-glazed casement window facing NW (328°)
5) Occupation | Opened Q3 2024; naming ceremony 6 Dec 2024 (S15)
6) Type of central air-conditioning | Not applicable - unitary window AC (room) and split AC (kitchen)
7) Weekly occupied hours of the room | 103
Daily average no. of occupants | 2
Occupant density (m² per person) | 7.5
Part 1 - (B)(II) Building services installation of the audited unit
Equipment (type code) | Cooling | Compressor | Refrigerant | Rated capacity (kW) | Input power (kW) | Qty | COP (kW/kW)
Window AC (R - room type) | A (air-cooled) | UA (inverter rotary) | R32 | 3.34 | 1.192 | 1 | 2.802
Total lighting power of room (kW) (EAC Clause 8.1(f)) | 0.06
Part 2 - Historical energy consumption analysis (EAC Clause 8.1(g))
1) Annual electricity, past 1st 12-month (kWh/annum) | 1219.6108 | Past 2nd and 3rd 12-month periods: N/A (room occupied from Jan 2026; EAC 8.1(g)(i))
2) Annual energy other than electricity (MJ/annum) | 0 | No Towngas or LPG
3) Annual total energy (MJ/annum) | 4390.5989
4) Annual EUI (MJ/m²/annum) | 292.7066 | Equals kWh/m²/annum x 3.6
5) Monthly EUI (MJ/m²/month), typical year
| Jan | Feb | Mar | Apr | May | Jun
| 16.8677 | 16.0613 | 16.8677 | 16.5989 | 32.2304 | 31.9616
| Jul | Aug | Sep | Oct | Nov | Dec
| 32.2304 | 32.2304 | 31.9616 | 32.2304 | 16.5989 | 16.8677
6) Annual breakdown (MJ/annum)
| Air-conditioning | Lighting | Lift & escalator | Others
| 3234.2789 | 420.48 | 0 | 735.84
7) Energy supplied by shared building services (washroom, kitchen, laundry) as % of household total | Jul: 52.85%
8) Energy bill reference month | Jul: September 2026 (Octopus pre-paid AC; no utility bill)
Part 3 - Energy Management Opportunities (EMO) | bar: Jul to Nov
Summary | Jul: Category I; Aug: Category II; Sep: Category III
No. of EMOs | Jul: 8; Aug: 6; Sep: 4
Summary | Lighting | Air-conditioning | Electrical | Lift/Escalator | Others
No. of EMOs | 1 | 8 | 2 | 0 | 7
Ref. | Jul: Category; Aug: Type; Sep: Description of EMO (EAC Clause 8.1(l)(i))
EMO-01 | Jul: I; Aug: AC; Sep: Raise the AC set-point from 25 °C to 26 °C and keep the 20 W desk fan running for air movement
EMO-02 | Jul: I; Aug: AC; Sep: Use the AC's built-in timer to switch off 2 h before waking in hot months (12 to 10 h/day)
EMO-03 | Jul: I; Aug: AC; Sep: Clean the AC filter fortnightly in summer, wipe the soiled louvres, close the curtain against late-afternoon NW sun
EMO-04 | Jul: I; Aug: LG; Sep: Use the desk task lights instead of both ceiling battens for 3 of the 6 lit hours
EMO-05 | Jul: I; Aug: Others; Sep: Shorten showers from 5 to 4 minutes
EMO-06 | Jul: I; Aug: Others; Sep: Lower the delivered shower temperature from 40 °C to 38 °C (turn the heater dial down)
EMO-07 | Jul: I; Aug: EL; Sep: Laptop power management: lower brightness, sleep after 10 min idle, battery-saver mode
EMO-08 | Jul: I; Aug: Others; Sep: Cook with lids, match pan to the induction zone, batch-cook two meals per session
EMO-09 | Jul: II; Aug: AC; Sep: Washroom exhaust fan: replace 24 h running with an occupancy / humidistat run-on control (~8 h/day)
EMO-10 | Jul: II; Aug: AC; Sep: Kitchen AC: 7-day timer + occupancy interlock, set-point locked at 25.5 °C (8 to 5 h/day hot, 4 to 2 h/day cool)
EMO-11 | Jul: II; Aug: Others; Sep: Water dispenser: enable night set-back / timer on hot and ice tanks (00:00-06:00)
EMO-12 | Jul: II; Aug: Others; Sep: Fit a WELS Grade-1 low-flow showerhead (9 to 7 L/min) in the shared washroom
EMO-13 | Jul: II; Aug: AC; Sep: Annual professional clean of the window-AC coil and louvres (heavy soiling seen in photo 03b)
EMO-14 | Jul: II; Aug: EL; Sep: Buy a plug-in power meter (about HK$120) to measure the laptop, fan and AC and verify savings (EAC §7.6.3)
EMO-15 | Jul: III; Aug: Others; Sep: Replace 24.4 kW instantaneous shower heaters with central air-source heat-pump water heating (COP about 3.5) and storage
EMO-16 | Jul: III; Aug: AC; Sep: Replace the Grade-1 window AC (CSPF 4.66) with a best-in-class split unit (CSPF about 7.5)
EMO-17 | Jul: III; Aug: AC; Sep: Solar-control film on the NW single glazing (1.55 m²)
EMO-18 | Jul: III; Aug: Others; Sep: Expand rooftop solar PV under the CLP Feed-in Tariff (the village already has 110 panels)

## EE-EAes_Entry_Guide
Entry guide - copy these values into the official EMSD form EE-EAes (V.2)
Open 2_EE-EAes2018 (V.0)_SEE6115-8115.xls in Excel with macros ENABLED (the form hides its sheets otherwise). Type each value into the cell shown; tick-boxes are listed as 'Tick'. Values link to this workbook.
Form sheet | Cell | Field on the form | Value to enter | Note
Part 1(A) | C15 | Name of building | Hall 13, CityU Lee Shau Kee Student Residence Village - Room 1003B, 10/F (voluntary home audit)
Part 1(A) | C16 | Address of building | Ma On Shan, New Territories, Hong Kong
Part 1(A) | H17 | 1) Date of commencement | 01/01/2026 | dd/mm/yyyy
Part 1(A) | H19 | 2) Date of completion | 11/10/2026 | dd/mm/yyyy
Part 1(A) | G21 / J21 | 3) Form validity (issued / expired) | N/A | Not issued under Cap. 610
Part 1(A) | H23 | 4) Report reference no. | SEE8115-HEA-2026-01
Part 1(A) | Tick-box | 5) Import / export energy? | Tick 'No'
Part 1(B)(I) | Tick-boxes | 1)(a) Type of building | Leave unticked | Only commercial types are offered; explain in H6
Part 1(B)(I) | H6 | 1)(a) free-text cell | Residential student hostel (not prescribed under Cap. 610)
Part 1(B)(I) | H7 | 1)(b) Common area % | 0
Part 1(B)(I) | H8 | 1)(c) No. of blocks | 1 | Audited unit only
Part 1(B)(I) | H9 | 2) Total internal floor area (m2) | 15
Part 1(B)(I) | H10 | 3) No. of floors | 10/F (audited unit)
Part 1(B)(I) | H11 | 4) Major type of facade | MiC concrete modules; single-glazed aluminium windows (NW)
Part 1(B)(I) | H12 | 5) Date of occupation | Q3 2024 (opened)
Part 1(B)(I) | Tick-box | 6) Type of central AC | Tick 'Not applicable' | Unitary window AC only
Part 1(B)(I) | G60 | 8)(f) Others - General, AC: % area | 100% | Whole room is air-conditioned
Part 1(B)(I) | H60 | 8)(f) weekday hours (hrs/week) | 65
Part 1(B)(I) | I60 | 8)(f) weekend hours (hrs/week) | 38
Part 1(B)(I) | H23 | 7)(f) Others - average weekly operating hours | 103
Part 1(B)(I) | I23 | 7)(f) Others - daily average occupants | 2
Part 2 | E2 | 1) Electricity, past 1st 12-month (kWh/annum) | 1219.6 | Room 1003B boundary
Part 2 | G2 / I2 | 1) Past 2nd and 3rd 12-month | N/A | Occupied from Jan 2026 (EAC 8.1(g)(i))
Part 2 | E5 | 2) Other energy, past 1st 12-month (MJ/annum) | 0 | No Towngas / LPG
Part 2 | G5 / I5 | 2) Past 2nd and 3rd 12-month | N/A
Part 2 | C14 | 5) Monthly EUI - 1st month (Oct) | 32.23 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | E14 | 5) Monthly EUI - 2nd month (Nov) | 16.6 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | G14 | 5) Monthly EUI - 3rd month (Dec) | 16.87 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | I14 | 5) Monthly EUI - 4th month (Jan) | 16.87 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | C16 | 5) Monthly EUI - 5th month (Feb) | 16.06 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | E16 | 5) Monthly EUI - 6th month (Mar) | 16.87 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | G16 | 5) Monthly EUI - 7th month (Apr) | 16.6 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | I16 | 5) Monthly EUI - 8th month (May) | 32.23 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | C18 | 5) Monthly EUI - 9th month (Jun) | 31.96 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | E18 | 5) Monthly EUI - 10th month (Jul) | 32.23 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | G18 | 5) Monthly EUI - 11th month (Aug) | 32.23 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | I18 | 5) Monthly EUI - 12th month (Sep) | 31.96 | MJ/m2/month; 12th month = reference month (Sep 2026)
Part 2 | C20 | 6) Air-conditioning (MJ/annum) | 3234 | Incl. desk fan
Part 2 | E20 | 6) Lighting (MJ/annum) | 420
Part 2 | G20 | 6) Lift & escalator (MJ/annum) | 0 | Not applicable
Part 2 | I20 | 6) Others (MJ/annum) | 736 | Laptops, phones
Part 2 | I22 | 7) Energy supply from CBSI (%) | N/A | Shared-services share is reported in the report instead
Part 2 | I24 | 8) Energy bill reference month | 30/09/2026 | Octopus pre-paid AC; no utility bill
Part 3 | A9 | EMO slot 1 - reference | EMO-01
Part 3 | Row 9 tick-boxes | EMO slot 1 - category / type | Tick Category I and type AC
Part 3 | H9 | EMO slot 1 - description | Raise the AC set-point from 25 °C to 26 °C and keep the 20 W desk fan running for air movement. Saving about 24 kWh/yr (household share).
Part 3 | A11 | EMO slot 2 - reference | EMO-02
Part 3 | Row 11 tick-boxes | EMO slot 2 - category / type | Tick Category I and type AC
Part 3 | H11 | EMO slot 2 - description | Use the AC's built-in timer to switch off 2 h before waking in hot months (12 to 10 h/day). Saving about 100 kWh/yr (household share).
Part 3 | A13 | EMO slot 3 - reference | EMO-03
Part 3 | Row 13 tick-boxes | EMO slot 3 - category / type | Tick Category I and type AC
Part 3 | H13 | EMO slot 3 - description | Clean the AC filter fortnightly in summer, wipe the soiled louvres, close the curtain against late-afternoon NW sun. Saving about 41 kWh/yr (household share).
Part 3 | A15 | EMO slot 4 - reference | EMO-04
Part 3 | Row 15 tick-boxes | EMO slot 4 - category / type | Tick Category I and type LG
Part 3 | H15 | EMO slot 4 - description | Use the desk task lights instead of both ceiling battens for 3 of the 6 lit hours. Saving about 44 kWh/yr (household share).
Part 3 | A17 | EMO slot 5 - reference | EMO-05
Part 3 | Row 17 tick-boxes | EMO slot 5 - category / type | Tick Category I and type Others
Part 3 | H17 | EMO slot 5 - description | Shorten showers from 5 to 4 minutes. Saving about 127 kWh/yr (household share).
Part 3 | A19 | EMO slot 6 - reference | EMO-06
Part 3 | Row 19 tick-boxes | EMO slot 6 - category / type | Tick Category I and type Others
Part 3 | H19 | EMO slot 6 - description | Lower the delivered shower temperature from 40 °C to 38 °C (turn the heater dial down). Saving about 77 kWh/yr (household share).
Part 3 | A21 | EMO slot 7 - reference | EMO-07
Part 3 | Row 21 tick-boxes | EMO slot 7 - category / type | Tick Category I and type EL
Part 3 | H21 | EMO slot 7 - description | Laptop power management: lower brightness, sleep after 10 min idle, battery-saver mode. Saving about 28 kWh/yr (household share).
Part 3 | A23 | EMO slot 8 - reference | EMO-09
Part 3 | Row 23 tick-boxes | EMO slot 8 - category / type | Tick Category II and type AC
Part 3 | H23 | EMO slot 8 - description | Washroom exhaust fan: replace 24 h running with an occupancy / humidistat run-on control (~8 h/day). Saving about 88 kWh/yr (household share).
Part 3 | A25 | EMO slot 9 - reference | EMO-10
Part 3 | Row 25 tick-boxes | EMO slot 9 - category / type | Tick Category II and type AC
Part 3 | H25 | EMO slot 9 - description | Kitchen AC: 7-day timer + occupancy interlock, set-point locked at 25.5 °C (8 to 5 h/day hot, 4 to 2 h/day cool). Saving about 33 kWh/yr (household share).
Part 3 | A27 | EMO slot 10 - reference | EMO-12
Part 3 | Row 27 tick-boxes | EMO slot 10 - category / type | Tick Category II and type Others
Part 3 | H27 | EMO slot 10 - description | Fit a WELS Grade-1 low-flow showerhead (9 to 7 L/min) in the shared washroom. Saving about 141 kWh/yr (household share).
Part 3 | A29 | EMO slot 11 - reference | EMO-15
Part 3 | Row 29 tick-boxes | EMO slot 11 - category / type | Tick Category III and type Others
Part 3 | H29 | EMO slot 11 - description | Replace 24.4 kW instantaneous shower heaters with central air-source heat-pump water heating (COP about 3.5) and storage. Saving about 455 kWh/yr (household share).
Part 3 | A31 | EMO slot 12 - reference | EMO-18
Part 3 | Row 31 tick-boxes | EMO slot 12 - category / type | Tick Category III and type Others
Part 3 | H31 | EMO slot 12 - description | Expand rooftop solar PV under the CLP Feed-in Tariff (the village already has 110 panels). Viability statement only - no saving claimed.
Part 3 | H31 (append) | Additional EMOs | Add: 'EMO-08, -11, -13, -14, -16 and -17 are listed in the attached EMO register.' | The form asks for an extra sheet if rows run out

## Photo_Log
Photo log - evidence for the inventory (files in photos/)
Ref | File | What it shows | Data extracted
01 | 01_room_overview.jpg | Room 1003B: twin beds, desks, ceiling LED battens, window AC above NW window | Room layout; equipment present
02a | 02a_window_view.jpg | Window and outlook over Tolo Harbour / Ma On Shan | Single glazing, dark aluminium frame, fly screen
02b | 02b_window_fixed_pane_measured.jpg | Bottom fixed pane measured 1.10 m x 0.17-0.19 m | Glazing area 0.209 m²
02c | 02c_window_casement_measured.jpg | Casement measured 0.53 m x 1.26 m = 0.67 m² | Two casements 1.34 m²
02d | 02d_compass_328NW.jpg | Compass 328° NW, 22°26'0"N 114°14'32"E, Ma On Shan, 44 m | Orientation and location
02e | 02e_curtain_closed.jpg | Full-height grey curtain closed; AC at upper left | Internal shading
03a | 03a_ac_specification.jpg | Midea MW-12CRF8E specification / energy label data | 3.34 kW, 1,192 W, R32, Grade 1, 362 kWh, CSPF 4.66
03b | 03b_ac_front_louvres.jpg | AC front: dark deposits on discharge louvres; Eco, Timer, Dry modes | Maintenance finding; controls available
05a | 05a_ceiling_led_battens.jpg | Two linear LED ceiling battens | Lighting inventory
05b | 05b_desk_led_and_fan.jpg | Under-shelf LED desk light and desk fan | Task lighting
06a | 06a_laptop_adapter_65W.jpg | HP 65 W adapter TPN-CA17, Efficiency Level VI | Laptop power
06b | 06b_desk_fan_label_20W.jpg | Fan label: ZW02-180, 180 mm, 20 W, 220 V | Fan power
08a | 08a_water_heater_DHB-E.jpg | Stiebel Eltron DHB-E electronic instantaneous heater, 30-60 °C dial | Hot-water system type
08b | 08b_washroom_downlights.jpg | Two LED downlights, exposed services, sensor | Washroom lighting
08c | 08c_washroom_light_and_fan.jpg | Downlight and window exhaust fan | Washroom lighting / ventilation
08d | 08d_washroom_exhaust_fan.jpg | J.E.E. window exhaust fan (runs 24 h) | Ventilation finding
08e | 08e_water_heater_spec.jpg | Heater specification: 380 V, max 60 °C | Electrical supply
09a | 09a_dispenser_spec.jpg | Aquatek AQ-1323T: 750 W heater, 160 W compressor, 10 L hot / 7.9 L cold / 3 L ice | Dispenser ratings
09b | 09b_water_dispenser.jpg | Dispenser in kitchen, hot water at 98 °C; SRO cleaning notice | Standing losses
09c | 09c_induction_cooker_spec.jpg | Philips HD4911: 2,100 W, EEL Grade 2 | Cooking power
09d | 09d_induction_cooker_product.jpg | Philips 5000 Series HD4911/80 (retailer image) | Model identification
09e | 09e_induction_energy_label.jpg | Energy label Grade 2, thermal efficiency 88.1% (I220011/22) | Cooking efficiency
09f | 09f_kitchen_split_ac.jpg | Toshiba split AC in kitchen (also used as photo 12 - left on 8 h+) | Kitchen AC
09g | 09g_kitchen_ac_energy_label.jpg | Label: 688 kWh/yr @1,200 h, 7.00 kW, R410A, Grade 1 | Kitchen AC energy
09h | 09h_microwave.jpg | Toshiba MW2-MM24PC 24 L, 800 W output | Kitchen inventory
09i | 09i_fridge_energy_label.jpg | Panasonic NR-BV361B: Grade 1, 263 kWh/yr, 233 + 99 L | Refrigeration energy

## Sources
Sources and references
ID | Short name | Citation | URL
S1 | EAC 2018 | EMSD (2018) Code of Practice for Building Energy Audit (EAC 2018), Buildings Energy Efficiency Ordinance (Cap. 610). Course file EAC_2018.pdf.
S2 | HK GHG Guidelines | EPD & EMSD (2010) Guidelines to Account for and Report on Greenhouse Gas Emissions and Removals for Buildings (Commercial, Residential or Institutional Purposes) in Hong Kong. Course file.
S3 | EE-EAes form | EMSD Technical Form EE-EAes (V.2) - Executive Summary of Energy Audit Report. Course file 2_EE-EAes2018 (V.0)_SEE6115-8115.xls.
S4 | Home Energy Audit Tool | Penn State / SMARTdwell Home Energy Audit Tool (course version). Course file 1_SEE6115-8115_Home Energy Audit Tool.xlsx.
S5 | CLP ESG Data Hub 2025 | CLP Holdings (2026) Sustainability Report 2025 - ESG Data Hub: CO2e emissions intensity of electricity sold by CLP Power Hong Kong = 0.34 kg/kWh (2025); 0.38 (2024); 0.39 (2023). | https://sustainability.clpgroup.com/en/2025/esg-data-hub
S6 | CLP 2026 tariff | CLP Power (2025) 2026 Tariff Adjustment - Average Net Tariff 140.6 cents/kWh (Basic Tariff 101.2 + Fuel Cost Adjustment 39.4). | https://www.clp.com.hk/en/clp-power-tariff-adjustment-2026
S7 | news.gov.hk 2026 tariffs | news.gov.hk (18 Nov 2025) 2026 electricity tariffs reduced - typical 3-person household consuming 275 kWh/month. | https://www.news.gov.hk/eng/2025/11/20251118/20251118_171441_586.html
S8 | HKO normals | Hong Kong Observatory - Climatological normals 1991-2020 (10-day and half-monthly mean air temperature, HKO Headquarters). | https://www.hko.gov.hk/en/cis/normal/1991_2020/15day_normal.htm
S9 | EMSD Energy Label - RAC | EMSD Mandatory Energy Efficiency Labelling Scheme - Room air conditioners: annual energy consumption stated on the label is based on 1,200 hours/year of operation. | https://www.emsd.gov.hk/energylabel/en/households/rac/eels_ac_eot_popup.htm
S10 | HK GHG inventory 2023 | Environment and Ecology Bureau (17 Apr 2025) Hong Kong GHG emission inventory 2023 (AR5): about 4.58 t CO2e per capita; electricity generation 61% of total. | https://www.news.gov.hk/eng/2025/04/20250417/20250417_120238_003.html
S11 | WSD unit electricity | Water Supplies Department Annual Report 2023/24 (as cited by HKGBC): unit electricity consumption 0.624 kWh/m3 fresh water, 0.362 kWh/m3 salt water. | https://hkgbc.org.hk/eng/resources/publications/HKGBC-Publication/Reports/green-building-in-action/references/2025.jsp
S12 | DSD unit electricity | Drainage Services Department Sustainability Report 2021/22 (as cited by HKU Water Centre): average unit electricity consumption of sewage treated 0.29 kWh/m3. | https://water.hku.hk/wp-content/uploads/2024/05/221200-ECF_Final-report_website-updates.pdf
S13 | HKU Water Centre | HKU Water Centre - Water conservation: per-capita domestic fresh water consumption 120.9 L/day (2023/24); ~85% of population uses seawater for flushing. | https://water.hku.hk/water-conservation/
S14 | LegCo LCQ5 (2012) | HKSAR Government (4 Jul 2012) LCQ5: raising indoor temperature by 1 degC can reduce AC electricity by around 3%; 25.5 degC guideline. | https://www.info.gov.hk/gia/general/201207/04/P201207040635.htm
S15 | CityU LSK Village | CityUHK (11 Dec 2024) Opening and Naming Ceremony for Lee Shau Kee Student Residence Village, Ma On Shan - 6 halls in 3 towers, ~2,100 residents, MiC with 1,300+ modules, opened Q3 2024, 110 rooftop PV panels. | https://www.cityu.edu.hk/en/media/press-release/2024/12/11/cityuhk-holds-opening-and-naming-ceremony-lee-shau-kee-student-residence-village
S16 | Stiebel Eltron DHB-E 27 | Stiebel Eltron DHB-E 27 SLi electronic instantaneous water heater: 27 kW at 400 V / 24.4 kW at 380 V, max 13.8 L/min (HK distributor listing). | https://hkele.com.hk/en/DHBE27SLI
S17 | MTR CDP 2022 | MTR Corporation CDP Climate Change 2022 response: Hong Kong rail intensity 0.0000723 t CO2e per passenger-km (1,079,402 t / 14.93 bn p-km). | https://www.mtr.com.hk/sustainability/assets/pdf/en/2022/MTR_CDP_Response.pdf
S18 | DESNZ 2025 factors | UK DESNZ (2025) Greenhouse gas reporting: conversion factors 2025 - Business travel (air), economy class, with radiative forcing (long-haul 0.11704 kg CO2e/p-km). | https://www.gov.uk/government/publications/greenhouse-gas-reporting-conversion-factors-2025
S19 | Scarborough et al. 2014 | Scarborough P. et al. (2014) Dietary greenhouse gas emissions of meat-eaters, fish-eaters, vegetarians and vegans in the UK. Climatic Change 125:179-192 (medium meat-eaters 5.63 kg CO2e/day). | https://www.oxfordmartin.ox.ac.uk/publications/dietary-greenhouse-gas-emissions-of-meat-eaters-fish-eaters-vegetarians-and-vegans-in-the-uk
S20 | ENERGY STAR water coolers | US EPA ENERGY STAR Water Coolers Specification V2.0: storage-type hot & cold units <= 0.87 kWh/day standby. | https://www.energystar.gov/sites/default/files/ES%20WC%20V2%200%20Spec.pdf
S21 | IPCC 2006 refrigerant | IPCC (2006) Guidelines Vol.3 Ch.7 - operating emission factor for residential & commercial AC 1-10% of charge per year (summary: ASHRAE Journal, Oct 2022). | https://www.ashrae.org/technical-resources/ashrae-journal/featured-articles/october-2022-analysis-of-refrigerant-use-for-ac-equipment-maintenance
S22 | CLP Feed-in Tariff | CLP Power (26 Apr 2022) Feed-in Tariff rates: HK$4/kWh (<=10 kW), HK$3/kWh (>10-200 kW), HK$2.5/kWh (>200 kW-1 MW). | https://www.clpgroup.com/content/dam/clp-group/channels/media/document/2022/20220426_en.pdf.coredownload.pdf
S23 | DEVB LCQ22 | Development Bureau LCQ22: median per-capita floor area of domestic households 172 sq ft (~16 m2), 2021 Population Census. | https://www.devb.gov.hk/en/sdev/press/index_id_11447.html
S24 | BEC 2021 LPD | EMSD - BEC 2021 vs BEC 2024 comparison: maximum lighting power density, Dormitory 6.2 W/m2 (BEC 2021), 6.1 W/m2 (BEC 2024). | https://emsd.gov.hk/beeo/en/pee/BEC2021vsBEC2024.pdf
S25 | HK hostel AC tariffs | Comparator hostel AC charges: HKU Jockey Club Student Village IV HK$2.31/kWh (2025/26); CUHK hostels HK$1.2/kWh. | https://wys.cuhk.edu.hk/college-life-support/information-for-residents/
S26 | LBNL coil fouling | Siegel J. et al. (2002) Dirty air conditioners: energy implications of coil fouling, LBNL - typical efficiency/capacity degradation < 5%. | https://www.osti.gov/biblio/805122
S27 | Consumer Council 2026 | Consumer Council (May 2026) test of 13 x 1.5 HP Grade-1 inverter split ACs: CSPF 5.06-7.51 (RTHK report). | https://news.rthk.hk/rthk/en/component/k2/1854660-20260514.htm
S28 | Midea MW-12CRF8E | Midea MW-12CRF8E 1.5 HP R32 inverter window AC - HK retailer specification (auditor screenshot + listing). | https://www.feverelectrics.com/en/products/midea-mw12crf8e-1-5hp-r32-inverter-window-type-air-conditioner
S29 | Auditor questionnaire & photos | Auditor's completed questionnaire (audit-inputs/QUESTIONNAIRE.md) and 26 site photographs (photos/), Oct 2026.
S30 | HKSAR Govt (2024) buildings ~90% of electricity | HKSAR Government press release (26 Jun 2024) Energy Saving and Decarbonisation for All campaign: buildings account for about 90% of Hong Kong's electricity consumption. | https://www.info.gov.hk/gia/general/202406/26/P2024062600623.htm
S31 | Climate Action Plan 2050 | HKSAR Government (8 Oct 2021) Hong Kong's Climate Action Plan 2050: carbon neutrality before 2050; halve emissions by 2035 vs 2005; cut residential-building electricity use 20-30% (commercial 30-40%) from 2015 levels by 2050, half of that by 2035. | https://www.info.gov.hk/gia/general/202110/08/P2021100800588.htm
S32 | US DOE Energy Saver | US Department of Energy, Energy Saver - Maintaining your air conditioner: replacing a dirty, clogged filter with a clean one can lower AC energy consumption by 5% to 15%. | https://www.energy.gov/energysaver/maintaining-your-air-conditioner